IKEJA CITY MALL — FIRE DETECTION AND ALARM SYSTEM OVERHAUL

Clarification Requirements — JML

# SECTION A — GENERAL REQUIREMENTS (ALL VENDORS)

## A1. Revised quotation for the entire project

Please re-submit a revised quotation covering the entire scope of the project. The revised quotation supersedes your original submission in full and will be the document evaluated.

## A2. Complete coverage of the bill of quantities

Every item listed in the Request for Proposal must be quoted, with complete technical details. Where you consider an item unnecessary, it must still be addressed in writing, with your engineering reasons stated, rather than omitted without comment.

## A3. Product identification for every quoted item

For each item quoted, state:

- the exact product model;

- the product code;

- the manufacturer reference or order number;

- the full technical specification;

- the specific variant being supplied;

- any further product identification that unambiguously defines the exact item proposed.

A quotation that describes a category of device rather than a specific part number cannot be evaluated against the other submissions received and will be treated as incomplete.

## A4. Technical assessment report

Alongside the revised quotation and invoice, submit a technical report based on the inspection you have already carried out at the mall. This is not additional work: the Request for Proposal already requires the contractor to assess the existing system and identify defective components.

## A5. Content of the technical assessment report

The report should address, as a minimum:

- the condition of the existing fire alarm system;

- the viability of the existing system;

- the extent of damage to the existing installation;

- the reasons for recommending the proposed overhaul;

- the engineering justification for the solution you propose;

- where you propose any variation from the specification in the Request for Proposal, the reasons for that variation;

- where you quote a particular variant of an item, the reasons that specific variant was selected.

## A6. Specification and variation of all equipment

For all equipment quoted, state clearly the exact specification and variation being supplied. Where a product family contains variants that differ in performance or price, identify which variant is offered and confirm the rate quoted corresponds to that variant.

## A7. Item 10 — Expansion Panel

Every vendor is required to address this item. State whether the additional expansion panel is technically required, having regard to the fact that the main 1–4 loop panel proposed appears capable of accommodating the estimated number of devices currently installed within the mall.

Your answer should be supported by engineering reasoning rather than asserted. Where you maintain the expansion panel is required, identify the constraint that drives it — loop loading by device type, current draw on visual alarm devices, loop length, zoning, network architecture, or the physical distribution of the building — and support it with a loop loading calculation.

## A8. Item 13 — Professional Services

Item 13 is to be revised. Rather than a lump sum, present the professional service fee as a reasonable percentage of the total value of Items 1 to 12, and state the percentage applied. Support it with a build-up showing the man-days, rates, commissioning duration and documentation effort on which the figure rests.

## A9. Manufacturer certification

Where you propose to retain the existing Gent system, confirm in writing whether you hold the qualifications and certifications required to program, commission and support a Gent fire alarm system. Name the certified commissioning engineer who would be assigned to this project and provide the certificate reference.

# SECTION B — CLARIFICATIONS SPECIFIC TO YOUR SUBMISSION

## B1. Specification of every quoted item

Provide complete specifications, product codes and variations for all items quoted, in the terms set out at A3. Where part numbers were stated in your original submission, carry them into the revised quotation and complete the remaining fields — variant, options, and technical specification — for each.

## B2. Item 10 — Expansion panel

Explain why no quotation was submitted against this item. The expansion panel is a specified line in the bill of quantities and your submission neither prices it nor comments on it.

## B3. Item 11 — Network card

- Explain why a network card was quoted despite no quotation being submitted for the expansion panel. The stated function of the network card is to connect panels to one another, and on your submission as it stands there is only one panel to connect.

- Clarify the intended application of the network card in the system you propose.

## B4. Engineering reasoning for the omission

Set out the engineering reasoning behind omitting the expansion panel. If your position is that the main panel alone is sufficient for the installed device population, state that expressly and support it with a loop loading calculation. An omission may well be technically correct, but it must be reasoned and stated rather than left to be inferred.

Confirm also whether the revised quotation prices the expansion panel or continues to omit it, so that the basis of your price is unambiguous.

## B5. Item 13 — Professional services

The sum of NGN 7,000,000 quoted equates to approximately 11.5% of Items 1 to 12, or some NGN 13,000 per device for the entire installation, testing, commissioning, documentation and training obligation. Revise this into a reasonable percentage of the total contract value for Items 1 to 12, supported by the build-up required at A8.

Confirm in doing so that the figure covers the whole of the obligation described at Item 13 and is fixed, and that no part of that obligation is expected to be recovered later as a variation.